## Summary
GHEtool is an open-source Python package designed for borefield sizing and temperature evolution evaluation . Currently, this tool employs the steady-state equivalent resistance method to calculate the heat transfer from the fluid to the borehole wall, which neglects the thermal capacity of the fluid, pipe, and grout. Consequently, heat is transferred immediately, without delay, from the fluid to the borehole wall, leading to an overestimation of the heat transfer peak to the surrounding ground. This often results in an oversized borefield, particularly for geothermal load profiles with high peak load variability. Meertens et al. [2] examined the impact of two short-term dynamic effects on borehole sizing and their significance for different geothermal load profiles. The first effect involved applying the cylindrical borehole correction of Li et al. [3], which extends the finite line model (currently used in GHEtool for calculating g-functions) to an infinite hollow cylinder within an infinite volume. This introduces a more realistic heat exchange surface between the borehole wall and the ground. The second effect investigated the replacement of the equivalent thermal resistance method with a dynamic model to describe the heat transfer within boreholes over small time scales. For this purpose, they used the 1D explicit numerical model of Xu and Spitler [4]. Their findings indicated that incorporating only the cylindrical borehole correction without considering any dynamic behavior results in a worse approximation than the base model implemented in GHEtool. Conversely, utilizing the dynamic model for small time scales provides the best approximation for heat transfer from the fluid to the ground. The relevance of this effect is highly dependent on the geothermal load profile; it significantly influences borefield size when the load profile exhibits high peak load variability. However, when the sizing is dominated by a large imbalance in the load profile, the effect is minimal. This paper introduces a comprehensive model that integrates the two aforementioned effects and compares it to the base model in GHEtool, as well as to sizing performed using the dynamic IBPSA borehole simulation model in Modelica.
References:
[1] Peere, W., Blanke, T.(2022). GHEtool: An open-source tool for borefield sizing in Python. Journal of Open Source Software, 7(76), 4406, https://doi.org/10.21105/joss.04406
[2] Meertens, L., Peere, W., and Helsen, L. (2024). Influence of short-term dynamic effects on geothermal borefield size. In _Proceedings of International Ground Source Heat Pump Association Conference 2024_. Montreal (Canada), 28-30 May 2024. https://doi.org/10.22488/okstate.24.000004
[3] Li et al
[4] Xu & Spitler
[x] Peere, W., L. Hermans, W. Boydens, and L. Helsen. 2023. Evaluation of the oversizing and computational speed of different open-source borefield sizing methods. BS2023 Conference, Shanghai, China, April

## Parameters
Summary of borefield parameters used for sizing |  |  | Yearly demand [MWh] and peak demand [kW] for the three different buildings
Description | Value | Unit |  |  | Auditorium | Office | Swimming pool
Borehole radius | 75 | mm | Yearly | Heating | 38.3 | 117.6 | 1965
Borehole burial depth | 4 | m |  | Cooling | 3.86 | 118.3 | 41.89
Borehole spacing | 6 | m | Peak | Heating | 32 | 214 | 540
Inner pipe radius | 15 | mm |  | Cooling | 90 | 371 | 106
Pipe spacing | 50 | mm
Outer pipe radius | 20 | mm
Ground conductivity | 3 | W/mK
Ground vol. heat capacity | 2.4 | MJ/m^3K
Undisturbed Ground temp. | 10 | °C
Ground heat flux | case dep. | W/m^2
Case 1 | 0 | W/m^2
Case 2/4 | 0.03 | W/m^2
Case 3/5 | 0.06 | W/m^2
Soil specific heat capacity | 1238 | J/kgK
Soil density | 1940 | kg/m^3
Grout conductivity | 1 | W/mK
Grout vol. heat capacity | 3.9 | MJ/m^3K
Grout specific heat capacity | 1925 | J/kgK
Grout density | 2026 | kg/m^3
Pipe conductivity | 0.4 | W/kK
Pipe vol. heat capacity | 1.54 | MJ/m^3K
Heat exchanger type | Double U-tube
Auditorium parameters
Borefield configuration | 5x4
Borefield HTF mass flow rate | 4 | kg/s
Office parameters
Borefield configuration | 10x10
Borefield HTF mass flow rate | 20 | kg/s
Swimming pool parameters
Borefield configuration | 15x20
Borefield HTF mass flow rate | 60 | kg/s
Note on B20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Adapt for Journal paper, wrong in conference paper
Note on B23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add this in journal paper, only used in GHEtool L4 ste (not in modelica)

## L4vsL4ste
Input variables |  |  | Results
Building load profile | Grounddata case | method | L [m] | Rb* | Tg [°C] | Time [s]
Auditorium | 1 | L4 | 126.83 | 0.146 | 10 | 1.78
|  | L4 ste | 99.15 | 0.142 | 10 | 1.36
| 2 | L4 | 143.99 | 0.15 | 10.7199 | 2.1
|  | L4 ste | 107.93 | 0.143 | 10.5397 | 3.72
| 3 | L4 | 184.27 | 0.16 | 11.8427 | 4.94
|  | L4 ste | 121.36 | 0.145 | 11.2136 | 5.21
| 4 | L4
L4 ste
Office | 1 | L4 | 134.93 | 0.148 | 10 | 2.51
|  | L4 ste | 126.27 | 0.146 | 10 | 4.85
| 2 | L4 | 155.02 | 0.152 | 10.7751 | 15.9
|  | L4 ste | 142.63 | 0.15 | 10.7132 | 6.34
| 3 | L4 | 209.25 | 0.167 | 12.0925 | 9.68
|  | L4 ste | 176.06 | 0.157 | 11.7606 | 12.46
| 4 | L4
L4 ste
Swimming pool | 1 | L4 | 349.46 | 0.219 | 10 | 4.68
|  | L4 ste | 347.27 | 0.218 | 10 | 31.19
| 2 | L4 | 277.85 | 0.19 | 11.3892 | 4.41
|  | L4 ste | 275.87 | 0.189 | 11.3794 | 17.37
| 3 | L4 | 240.57 | 0.177 | 12.4057 | 3.32
|  | L4 ste | 239.86 | 0.176 | 12.3986 | 10.74
| 4 | L4 | 215.14 | 0.169 | 13.227 | 6.46
|  | L4 ste | 214.62 | 0.168 | 13.2192 | 6.46
Note on B11: Lone Meertens: NOT possible due to high cooling load (limited by Tmax) --> GHEtool.VariableClasses.BaseClass.UnsolvableDueToTemperatureGradient: No solution can be found due to the temperature gradient. Please increase the field size Gradient 2.2 still possible, but 3 is too much
Ground temperature cases
1. Constant ground temperature
2. Gradient of 1 K/100m in ground temperature = Geothermal heat flux of 0.03 W/m^2 (gradient/100 * k_s = 0.01 K/m * 3 W/mK)
3. Gradient of 2 K/100m in ground temperature = Geothermal heat flux of 0.06 W/m^2
4. Gradient of 3 K/100m in ground temperature = Geothermal heat flux of 0.09 W/m^2
Relationship gradient and geothermal heat flux:
geothermal gradient is equal to the geothermal heat flux divided by the Ground thermal conductivity k_s [W/mK] --> k_s = 3 W/mK
Example 3) gradient = 0.06 W/m^2 / (3 W/mK) = 0.02 K/m = 2 K/100m
Unsolved Questions:
1. Why Modelica gives bigger sizes when using constant ground temperature?? (Should expext lower, since dynamic behavior is taken into account and ground behaviour is the same)
2. Sizing with geothermal flux in GHEtool and then taken _Tg (average ground temperature) as input into constant ground temperature model in modelica. Is this accurate?
To Do's
Modelica:
*definitie g-functie: tov boorgatwand of grond?
* gradient model
* constante temperatuuur (grondtemperatuur zelf uitrekenen)
g-functie
* aanname constante boorgatwand temperatuur
* Dus gradient in rekening nemen niet correct.

## Modelica
Input variables | [9 empty] | Results
Building load profile | ground temp. case | L_start [m] | T_L [°C] | T_H [°C] | T_g [°C] | lifetime [years] | use_Rb | solver | Integration step | L [m] | Tmin [°C] | Tmax [°C] | number of iterations | time needed for sizing [min]
Auditorium | 1 | 100 | 3 | 17 | 10 | 20 | False | Euler | 15 | 88.3666 | 5.8853 | 16.9997 | 4 | 6.7603
|  | 150 | 3 | 17 | 10 | 20 | False | Euler | 15 | 88.366 | 5.8853 | 16.9997 | 5 | 8.1589
| 2 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 95.1979 | 6.5651 | 16.9996 | 5 | 8.1686
| 3 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 105.2628 | 7.4041 | 17.0014 | 6 | 9.3103
| 4 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 96.0715 | 6.6451 | 16.9997 | 5 | 8.0306
| 5 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 107.9726 | 7.6016 | 17.0009 | 7 | 10.8303
Office | 1 | 100 | 3 | 17 | 10 | 20 | False | Euler | 15 | 120.578 | 8.103 | 17.0004 | 4 | 8.9103
| 2 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 134.4181 | 8.8628 | 17.0008 | 7 | 14.1628
| 3 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 160.1081 | 9.907 | 17.0015 | 12 | 22.739
| 4 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 136.0574 | 8.9421 | 17.0004 | 7 | 14.235
| 5 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 168.4723 | 10.1724 | 17.0003 | 15 | 28.3189
Swimming pool | 1 | 100 | 3 | 17 | 10 | 20 | False | Euler | 15 | 336.5738 | 2.9998 | 9.8781 | 7 | 17.7627
| 2 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 277.5457 | 2.9998 | 11.0755 | 5 | 13.7309
| 3 | 100 | 3 | 17 | 10+grad | 20 | False | Euler | 15 | 242.8044 | 3.0008 | 12.0221 | 7 | 17.7287
| 4 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 272.0111 | 2.9993 | 11.2381 | 6 | 15.4314
| 5 | 100 | 3 | 17 | updated | 20 | False | Euler | 15 | 236.6244 | 2.998 | 12.2448 | 7 | 17.6862
Using constant ground temperature equal to 10°C
Using gradient (0.01 K/m for case 2 and 0.02K/m for case3) with surface temp of 10°C
Using constant ground temperature model and update Tg each iteration with _Tg (average Tg) from GHEtool (same gradients as above)
Note on AA2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Wrong results, using AntiFreeze instead of water as HTF in boreholes. How can this big difference be explained??
Note on B12: Lone Meertens: Case dependent - case 1: flux = 0 - case 2/4: flux = 0.02 - case 3/5: flux = 0.06
Ground temperature cases
1. Constant ground temperature
2. Gradient of 1 K/100m in ground temperature (gradient model)
3. Geothermal heat flux of 0.06 W/m^2
4. Equivalent method (cst model) for gradient 1 K/100m
5. Equivalent method (cst model) for gradient 2 K/100m = 0.06 W/m^m flux
Prelimanary Conclusions
1. Very good estimated guess is needed to reduce number of iterations and consequently time needed for sizing
Lessons Learnt:
1. Use Water no AntiFreeze as HTF in boreholes, Antifreeze gives very wrong results (see right) (why?). For constant temperature case the following required lenghts were obtained with anaitfreeze: 162.9, 192.2 and 358.0
2. Use small enough integration time step when using Euler (30s is aalready to big sometimes, get stuck in fluid temperature minimal constraint)

## GHEvsMod
Building load profile | Ground Temperature Case | Resulting size L [m] |  |  | Relative difference (L4-Lmodelica)/Lmodelica
|  | L4 | L4 ste | Lmod | L4 | L4 ste
Auditorium | 1 | 126.83 | 99.15 | 88.37 | 43.5216 | 12.1987
| 2 | 143.99 | 107.93 | 95.198 | 51.2532 | 13.3742
| 3 | 184.27 | 121.36 | 105.26 | 75.0618 | 15.2955
| 4 | 143.99 | 107.93 | 96.07 | 49.8803 | 12.3452
| 5 | 184.27 | 121.36 | 107.97 | 70.6678 | 12.4016
Office | 1 | 134.93 | 126.27 | 120.58 | 11.9008 | 4.7189
| 2 | 155.02 | 142.63 | 134.42 | 15.3251 | 6.1077
| 3 | 209.25 | 176.06 | 160.11 | 30.6914 | 9.9619
| 4 | 155.02 | 142.63 | 136.06 | 13.935 | 4.8288
| 5 | 209.25 | 176.06 | 168.47 | 24.2061 | 4.5053
Swimming pool | 1 | 349.46 | 347.27 | 336.57 | 3.8298 | 3.1791
| 2 | 277.85 | 275.87 | 277.55 | 0.10809 | -0.6053
| 3 | 240.57 | 239.86 | 242.8 | -0.91845 | -1.2109
| 4 | 277.85 | 275.87 | 272.01 | 2.147 | 1.4191
| 5 | 240.57 | 239.86 | 236.62 | 1.6693 | 1.3693
Using constant ground temperature equal to 10°C
Using gradient (0.01 K/m for case 2 and 0.02K/m for case3) with surface temp of 10°C
Using constant ground temperature model and update Tg each iteration with _Tg (average Tg) from GHEtool (same gradients as above)
Opmerkingen
1) L4 ste bevat cilindrische correctie (ook voor lange termijn), g-functie dus niet hetzelfde op lange termijn als L4.
2) Resultaten voor Lmod (case 2) momenteel obv gradient model. Deze verondersteld verschillende Tb en neemt dan gemiddelde? Dit gaat in tegen de definite van g-functie (constante boorgatwandtemperatuur), reproduceer resultaten met constant grondtemepratuur model met update obv GHEtool
3) Hoe lost GHEtool het probleem in 2) eigenlijk op?

## Results
L4 GHEtool standard
| L [m] | tijd [s] | Rb* [m.K/W]
Auditorium | 184.27 | 6.55 | 0.16
Office | 209.25 | 14.44 | 0.167
Swimming pool | 240.57 | 3.97 | 0.177
| L4 Dynamic model switching to FLS+CC |  |  |  | L4 Dynamic model switching to FLS+CC
| L [m] | tijd [s] | Rb* [m.K/W] | tswitch [h] | L [m] | tijd [s] | Rb* [m.K/W] | tswitch [h]
Auditorium | 118.13 | 6.39 | 0.145 | 27.33 | 118.17 | 5.3 | 0.145 | 17.06
Office | 173.7 | 15.72 | 0.157 | 41.1 | 173.44 | 13.78 | 0.167 | 25.9
Swimming pool | 239.8 | 12.77 | 0.176 | 134.87 | 239.8 | 10.22 | 0.176 | 79.133
Modelica
| L [m] | tijd [s] | Rb* [m.K/W]
Auditorium
Office
Swimming pool
Necessary sizing time gives misleading values
Initial guess determines number of iteration needed to size borefield. When initial guess is closer to final value, total number of needed iteriation can be smaller. Therefore the sizing time for short-term method can be lower than for the standard L4 method. Initial guess for al options was 100m